## 2013 Britannia
2013 City of Ottawa Drinking Water Quality : Physical, Chemical, Microbiological & Radiological
Britannia Water Purification Plant & Distribution System
PARAMETER | BRITANNIA |  |  | BRITANNIA |  |  | CENTRAL |  |  | M.A.C.* | TOTAL # of RESULTS
(mg/L unless otherwise stated) | RAW (RIVER) WATER |  |  | TREATED WATER |  |  | DISTRIBUTION |  |  | TREATED | Brit Raw Water |  | Brit Treated Water |  | Central Dist
| MIN. | MAX. | AVERAGE | MIN. | MAX. | AVERAGE | MIN. | MAX. | AVERAGE | WATER | # Tested | # Used | # Tested | # Used | # Tested | # Used
PHYSICAL
Colour, T.C.U. | 32 | 61 | 42 | < 3 | 6.8 | < 3 | < 3 | 5 | < 3 | 5.0 (AO) | 13 | 13 | 732 | 732 | 7 | 7
Turbidity, N.T.U. | 1.22 | 10.47 | 3.38 | 0.02 | 0.09 | 0.06 | 0.06 | 7.02 | 0.21 | 5.00 (AO) | 729 | 729 | 728 | 728 | 2883 | 2883
Temperature, oC | < 0.1 | 26.1 | 9.9 | --- | --- | --- | 0.2 | 26.4 | 12.7 | 15.0 (AO) | 728 | 728 | --- | --- | 2803 | 2803
UV 254 (cm-1) | 0.228 | 0.382 | 0.284 | 0.06 | 0.06 | 0.06 | 0.04 | 0.07 | 0.051 |  | 728 | 728 | 4 | 4 | 7 | 7
CHEMICAL INORGANIC
pH | 6.9 | 7.66 | 7.35 | 9.11 | 9.57 | 9.36 | 8.75 | 9.89 | 9.32 | 6.5-8.5 (OG) | 732 | 732 | 729 | 729 | 2799 | 2799
Total Alkalinity, as CaCO3 | 15 | 44 | 28 | 22 | 52 | 34 | 29 | 30 | 30 | 30-500 (OG) | 745 | 745 | 744 | 744 | 5 | 5
Total Hardness, as CaCO3 ** | 22.7 | 40.9 | 31.8 | 22.7 | 40 | 31.8 | 20.4 | 51.9 | 31.1 | 80-100 (OG) | 14 | 14 | 14 | 14 | 251 | 251 | DWSP did 2 total hardness
Calcium Hardness, as CaCO3 ** | 15.7 | 29 | 22.1 | 15.7 | 28.5 | 22.2 | 13.7 | 29.7 | 22.1 |  | 13 | 13 | 13 | 13 | 249 | 249 | but no Ca or Mg hardness
Magnesium Hardness, as CaCO3 ** | 7 | 11.9 | 9.3 | 7 | 11.5 | 9.2 | 939 | 11.9 | 8.9 |  | 13 | 13 | 13 | 13 | 249 | 249
Ammonia Nitrogen, N | < 0.01 | 0.09 | 0.02 | < 0.01 | 0.08 | < 0.01 | < 0.01 | 0.12 | 0.01 |  | 733 | 733 | 744 | 744 | 257 | 257
Total Kjeldahl Nitrogen, N | 0.25 | 0.57 | 0.31 | 0.3 | 0.48 | 0.36 | 0.26 | 0.67 | 0.37 |  | 12 | 12 | 12 | 12 | 355 | 355
Organic Nitrogen, N** | 0.24 | 0.56 | 0.29 | 0.3 | 0.48 | 0.35 | 0.23 | 0.56 | 0.35 | 0.15 (OG) | 12 | 12 | 12 | 12 | 229 | 229
Nitrates, N | 0.07 | 0.25 | 0.15 | 0.09 | 0.26 | 0.16 | 0.07 | 0.3 | 0.14 | 10 | 15 | 15 | 15 | 15 | 357 | 357
Nitrites, N | < 0.02 | < 0.02 | < 0.02 | < 0.02 | < 0.02 | < 0.02 | < 0.02 | 0.14 | < 0.02 | 1 | 15 | 15 | 15 | 15 | 357 | 357
Suspended Solids | < 2 | 65 | 8 | --- | --- | --- | --- | --- | --- |  | 11 | 11 | --- | --- | --- | ---
Langelier's Index** | -2.2 | -1.4 | -1.7 | -2.2 | -1.4 | -1.7 | --- | --- | --- |  | 13 | 13 | 13 | 13 | --- | ---
Conductivity Micromhos/cm @ 25 oC | 58 | 104 | 77 | 108 | 183 | 146 | 139 | 144 | 142 |  | 15 | 15 | 15 | 15 | 5 | 5
Chloramine (Total chlorine) | --- | --- | --- | 1.54 | 2.53 | 1.9022 | 0.1 | 2.3 | 1.5421 | 3 | --- | --- | 729 | 729 | 9875 | 9875
C-T Disinfection** (mg/L-min) | --- | --- | --- | 32.1 | 130.1 | 62.0035 | --- | --- | --- |  | --- | --- | 1453 | 1453 | --- | ---
Log Giardia Disinfection | --- | --- | --- | 0.8 | 9.79 | 2.9745 | --- | --- | --- | 0.5-log | --- | --- | 1453 | 1453 | --- | ---
Log Virus Disinfection | --- | --- | --- | 3.66 | >> 20.0 | > 20.0 | --- | --- | --- | 3.0-log | --- | --- | 1453 | 1453 | --- | ---
Aluminium, Al | 0.104 | 0.6653 | 0.22527 | 0.0317 | 0.2755 | 0.11952 | 0.0165 | 0.2876 | 0.093586 | 0.100 (OG) | 15 | 15 | 15 | 15 | 259 | 259
Antimony, Sb | < 0.0002 | < 0.0002 | < 0.0002 | < 0.0002 | 0.0011 | < 0.0002 | < 0.0002 | 0.001 | < 0.0002 | 0.006 | 15 | 12 | 15 | 15 | 259 | 259
Arsenic, As | < 0.0002 | 0.001 | 0.00064 | < 0.0002 | 0.0007 | 0.00028667 | < 0.0002 | 0.0008 | 0.00028069 | 0.010 / 0.025 | 15 | 15 | 15 | 15 | 259 | 259
Barium, Ba | 0.0137 | 0.0313 | 0.017227 | 0.0119 | 0.0171 | 0.014213 | 0.0106 | 0.0195 | 0.014254 | 1 | 15 | 15 | 15 | 15 | 259 | 259
Beryllium, Be | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | 0.0001 | < 0.0001 |  | 15 | 15 | 15 | 15 | 259 | 259
Boron, B | 0.0048 | 0.0113 | 0.0075333 | 0.0046 | 0.0082 | 0.0069333 | 0.0044 | 0.0279 | 0.0076398 | 5 | 15 | 15 | 15 | 15 | 259 | 259
Bromate, BrO3 **** | < 0.003 | < 0.003 | < 0.003 | < 0.003 | < 0.003 | < 0.003 | < 0.003 | < 0.003 | < 0.003 | 0.01 | 4 | 4 | 4 | 4 | 8 | 8
Bromide, Br **** | 0.02 | 0.024 | 0.02225 | 0.014 | 0.022 | 0.01725 | 0.011 | 0.019 | 0.01575 |  | 4 | 4 | 4 | 4 | 8 | 8
Cadmium, Cd | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | 0.005 | 15 | 15 | 15 | 15 | 259 | 259
Calcium, Ca | 6.3 | 11.6 | 8.8615 | 6.3 | 11.4 | 8.9 | 5.5 | 11.9 | 8.8687 |  | 13 | 13 | 13 | 13 | 249 | 249
Chlorate, ClO3 **** | < 0.01 | < 0.01 | < 0.01 | 0.07 | 0.16 | 0.105 | 0.05 | 0.22 | 0.12 | 1 | 4 | 4 | 4 | 4 | 8 | 8
Chloride, Cl | 2.4 | 8.3 | 3.64 | 4 | 10.2 | 5.6733 | 3.6 | 9.6 | 5.4552 | 250.0 (AO) | 15 | 15 | 15 | 15 | 357 | 357
Chlorite, ClO2 **** | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | 1 | 4 | 4 | 4 | 4 | 8 | 8
Chromium, Cr | 0.0003 | 0.0015 | 0.00065 | < 0.0001 | 0.0004 | 0.00017083 | < 0.0001 | 0.0022 | 0.00018123 | 0.05 | 15 | 12 | 15 | 12 | 259 | 253
Chlormium VI | 6e-05 | 9e-05 | 7.25e-05 | 4e-05 | 8e-05 | 5.75e-05 | --- | --- | --- |  | 4 | 4 | 4 | 4 | --- | ---
Cobalt, Co | < 0.0001 | 0.0006 | 0.00012 | < 0.0001 | 0.0002 | < 0.0001 | < 0.0001 | 0.0004 | < 0.0001 |  | 15 | 15 | 15 | 15 | 259 | 259
Copper, Cu | 0.0075 | 0.0373 | 0.020673 | < 0.0005 | 0.0019 | 0.00094333 | < 0.0005 | 0.0571 | 0.002867 | 1.0000 (AO) | 15 | 15 | 15 | 15 | 259 | 259
Cyanide, CN | < 0.002 | < 0.002 | < 0.002 | < 0.002 | < 0.002 | < 0.002 | < 0.002 | 0.002 | < 0.002 | 0.2 | 4 | 4 | 4 | 4 | 8 | 8
Dissolved Inorganic Carbon | 3.5 | 6.9 | 5.6333 | 4.5 | 7.2 | 6.2667 | --- | --- | --- |  | 3 | 3 | 3 | 3 | --- | ---
Dissolved Organic Carbon | 6.68 | 8.09 | 7.176 | 2.8 | 3.74 | 3.1353 | 2.98 | 3.14 | 3.048 | 5.0 (AO) | 15 | 15 | 15 | 15 | 5 | 5
Fluoride, F | 0.04 | 0.08 | 0.056667 | 0.58 | 0.792 | 0.68779 | 0.02 | 0.76 | 0.63464 | 1.5 | 15 | 15 | 735 | 735 | 248 | 248
Iron, Fe | 0.1375 | 1.094 | 0.29335 | < 0.006 | 0.014 | 0.00774 | < 0.006 | 0.2002 | 0.024253 | 0.300 (AO) | 15 | 15 | 15 | 15 | 258 | 258
Lead, Pb | < 0.0001 | 0.002 | 0.00033 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | 0.0032 | 0.00010753 | 0.01 | 15 | 15 | 15 | 15 | 259 | 259
Magnesium, Mg | 1.7 | 2.9 | 2.2569 | 1.7 | 2.8 | 2.2369 | 1.6 | 2.9 | 2.1614 |  | 13 | 13 | 13 | 13 | 249 | 249
Manganese, Mn | 0.0079 | 0.3368 | 0.033453 | 0.0011 | 0.0059 | 0.0030533 | 0.0003 | 0.028 | 0.0031216 | 0.050 (AO) | 15 | 15 | 15 | 15 | 259 | 259
Mercury, Hg | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | 0.001 | 12 | 12 | 12 | 12 | 252 | 252
Molybdenum, Mo | < 0.0005 | < 0.0005 | < 0.0005 | < 0.0005 | < 0.0005 | < 0.0005 | < 0.0005 | 0.0006 | < 0.0005 |  | 15 | 15 | 15 | 15 | 259 | 259
Nickel, Ni | < 0.0001 | 0.0065 | 0.00123 | < 0.0001 | 0.0013 | 0.00048 | < 0.0001 | 0.0426 | 0.00074324 |  | 15 | 15 | 15 | 15 | 259 | 259
Phosphates, PO4 | 0.0017 | 0.0058 | 0.0041333 | 0.0016 | 0.0043 | 0.0033333 | < 0.002 | 0.002 | < 0.002 |  | 3 | 3 | 3 | 3 | 78 | 78
Phosphorus (Total), P | --- | --- | --- | --- | --- | --- | < 0.005 | 0.01 | < 0.005 |  | --- | --- | --- | --- | 85 | 85
Potassium, K | 0.63 | 0.86 | 0.71462 | 0.61 | 0.76 | 0.66462 | 0.48 | 0.91 | 0.66787 |  | 16 | 16 | 16 | 16 | 159 | 159
Selenium, Se | < 0.0002 | 0.0006 | < 0.0002 | < 0.0002 | 0.0006 | 0.00022 | < 0.0002 | 0.0007 | < 0.0002 | 0.01 | 21 | 15 | 21 | 15 | 176 | 165
Silicate, Si02 | 2.2 | 2.52 | 2.3733 | 2.36 | 2.64 | 2.5067 | --- | --- | --- |  | 3 | 3 | 3 | 3 | --- | ---
Silver, Ag | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | 0.0002 | < 0.0001 | < 0.0001 | 0.0004 | < 0.0001 |  | 15 | 15 | 15 | 15 | 259 | 259
Sodium, Na | 2.6 | 6 | 3.3538 | 13 | 22.5 | 17 | 12.4 | 23.6 | 16.2863 | 20, 200(AO) | 13 | 13 | 13 | 13 | 249 | 249
Strontium, Sr | 0.0319 | 0.063 | 0.04136 | 0.0318 | 0.0623 | 0.041167 | 0.0297 | 0.1211 | 0.042447 |  | 15 | 15 | 15 | 15 | 259 | 259
Sulphate, SO4 | 4.7 | 7.2 | 5.6467 | 19.4 | 35.2 | 27.82 | 18.4 | 38.9 | 26.6328 | 500.0 (AO) | 15 | 15 | 15 | 15 | 357 | 357
Thallium, Tl | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 |  | 15 | 15 | 15 | 15 | 259 | 259
Tin, Sn | < 0.0002 | 0.0003 | < 0.0002 | < 0.0002 | 0.0011 | < 0.0002 | < 0.0002 | 0.0084 | < 0.0002 |  | 12 | 12 | 12 | 12 | 253 | 253
Titanium, Ti | 0.0033 | 0.0402 | 0.0095067 | < 0.0002 | < 0.0002 | < 0.0002 | < 0.0002 | 0.0046 | < 0.0002 |  | 15 | 15 | 15 | 15 | 259 | 259
Tungsten, W | < 0.0002 | 0.0005 | < 0.0002 | < 0.0002 | 0.0003 | < 0.0002 | < 0.0002 | 0.0006 | < 0.0002 |  | 12 | 12 | 12 | 12 | 253 | 253
Uranium, U | < 0.0001 | 0.0002 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | 0.0002 | < 0.0001 | 0.02 | 15 | 15 | 15 | 15 | 259 | 259
Vanadium, V | 0.0005 | 0.002 | 0.00067333 | < 0.0001 | 0.0006 | 0.00034 | < 0.0001 | 0.0005 | 0.00033378 |  | 15 | 15 | 15 | 15 | 259 | 259
Zinc, Zn | < 0.0005 | < 0.0005 | < 0.0005 | < 0.0005 | 0.0032 | 0.00094 | < 0.0005 | 0.0543 | 0.001466 | 5.000 (AO) | 15 | 15 | 15 | 15 | 259 | 259
Zirconium, Zr | 0.0001 | 0.0003 | 0.0002 | < 0.0001 | 0.0003 | < 0.0001 | < 0.0001 | 0.0003 | < 0.0001 |  | 12 | 12 | 12 | 12 | 253 | 253
Total Trihalomethanes *** | --- | --- | --- | 0.0208 | 0.0443 | 0.03428 | 0.0202 | 0.0542 | 0.0393 | 0.1 | 3 | 3 | 15 | 15 | 39 | 39
Haloacetic Acids (5) | --- | --- | --- | 0.0175 | 0.0317 | 0.0248 | 0.018 | 0.0455 | 0.0275 | 0.08 | --- | --- | 15 | 15 | 39 | 39
Haloacetic Acids (9) | --- | --- | --- | 0.0218 | 0.0365 | 0.0291 | 0.021 | 0.0512 | 0.0313 |  | --- | --- | 15 | 15 | 39 | 39
MICROBIOLOGICAL | MIN. | MAX. | AVERAGE | MIN. | MAX. | # >MAC | MIN. | MAX. | # >MAC
Total Coliforms (CFU/100 mL) | 8 | > 2420 | 821 | 0 | Positive | 1 | 0 | Positive | 15 | 0 | 365 | 365 | 1427 | 1427 | 4989 | 4989
E. Coli (CFU/100 mL) | 0 | 614 | 25 | 0 | 0 | 0 | 0 | Positive | 1 | 0 | 365 | 365 | 1427 | 1427 | 4989 | 4989
HPC (CFU/mL) | < 10 | > 3000 | 337 | < 10 | 120 | 0 | < 10 | 2000 | 13 | 500 (OG) | 53 | 53 | 212 | 212 | 2883 | 2883
| MIN. | MAX. | AVERAGE | MIN. | MAX. | AVERAGE | MIN. | MAX. | AVERAGE
Campylobacter (MPN/L) | 0 | 8.86 | 2.1329 | --- | --- | --- | --- | --- | --- |  | 12 | 12 | --- | --- | --- | ---
E. coli O157:H7 (MPN/L) | 0 | 0 | 0 | --- | --- | --- | --- | --- | --- |  | 12 | 12 | --- | --- | --- | ---
Enteric Virus (MPN/L) | 0 | 1.4 | 0.39833 | --- | --- | --- | --- | --- | --- |  | 9 | 9 | --- | --- | --- | ---
Cryptosporidium (No. per 100 L) | 0 | 14 | 1.925 | 0 | 0 | 0 | --- | --- | --- |  | 12 | 12 | 12 | 12 | --- | ---
Giardia (No. per 100L) | 0 | 17 | 5.8167 | 0 | 0 | 0 | --- | --- | --- |  | 12 | 12 | 12 | 12 | --- | ---
RADIOLOGICAL
Gross-Alpha Radioactivity (Bq/L) **** | < 0.04 | < 0.04 | < 0.04 | < 0.01 | 0.02 | < 0.01 | --- | --- | --- | 0.5 | 3 | 3 | 55 | 52 | --- | ---
Gross-Beta Radioactivity (Bq/L) | < 0.04 | < 0.04 | < 0.04 | < 0.01 | 0.049 | 0.032788 | --- | --- | --- | 1 | 3 | 3 | 55 | 52 | --- | ---
Tritium (Bq/L) | < 5.0 | < 5.0 | < 5.0 | < 3.0 | 7 | 4.4301 | --- | --- | --- | 7000 | 3 | 3 | 55 | 52 | --- | ---
Total # of Results | [10 empty] | 5940 |  | 13458 |  |  | 42609
* Guidelines for Canadian Drinking Water Quality (Health Canada) & Ontario Drinking Water Standards (Ministry of the Environment)
**calculated parameter
*** The reported Average Total THM value is an annual average of the maximum value observed in each quarter
**** Detection limits are different not the same for all sample locations for this parameter
MAC - Maximum Acceptable Concentration
MAC for Arsenic from the Guidelines for Canadian Drinking Water Quality is 0.010 mg/L, from the Ontario Drinking Water Standards is 0.025 mg/L | [9 empty] | mg/L = milligrams per Litre = parts per million (ppm)
< Indicates value below analytical detection limit | [9 empty] | TCU = true colour units
NL - No limit exists under provincial or federal drinking water guidelines | [9 empty] | NTU = nephelometric turbidity units
--- No data available (test not performed) | [9 empty] | Bq/L = Becquerels per Litre
AO = Aesthetic Objective
Average 2013 Water Production Rate: BRITANNIA = 145.0 ML/d; LEMIEUX = 130.3 ML/d; TOTAL = 275.3 ML/d | [9 empty] | OG = Operational Guideline

## 2013 Lemieux
2013 City of Ottawa Drinking Water Quality : Physical, Chemical, Microbiological & Radiological
Lemieux Island Water Purification Plant & Distribution System
PARAMETER | LEMIEUX ISLAND |  |  | LEMIEUX ISLAND |  |  | CENTRAL |  |  | M.A.C.* | TOTAL # of RESULTS
(mg/L unless otherwise stated) | RAW (RIVER) WATER |  |  | TREATED WATER |  |  | DISTRIBUTION |  |  | TREATED | Lem Raw Water |  | Lem Treated Water |  | Central Dist
| MIN. | MAX. | AVERAGE | MIN. | MAX. | AVERAGE | MIN. | MAX. | AVERAGE | WATER | # Tested | # Used | # Tested | # Used | # Tested | # Used
PHYSICAL
Colour, T.C.U. | 32 | 55 | 42 | < 3 | 4 | < 3 | < 3 | 5 | < 3 | 5.0 (AO) | 13 | 13 | 716 | 716 | 7 | 7
Turbidity, N.T.U. | 1.32 | 12 | 3.63 | 0.02 | 0.11 | 0.05 | 0.06 | 7.02 | 0.21 | 5.00 (AO) | 728 | 728 | 727 | 727 | 2883 | 2883
Temperature, oC | < 0.01 | 26.5 | 9.6 | --- | --- | --- | 0.2 | 26.4 | 12.7 | 15.0 (AO) | 728 | 728 | --- | --- | 2803 | 2803
UV 254 (cm-1) | 0.238 | 0.348 | 0.281 | 0.04 | 0.05 | 0.04 | 0.04 | 0.07 | 0.051 |  | 726 | 726 | 4 | 4 | 7 | 7
CHEMICAL INORGANIC
pH | 6.88 | 7.9 | 7.44 | 9.05 | 10.06 | 9.36 | 8.75 | 9.89 | 9.32 | 6.5-8.5 (OG) | 731 | 731 | 727 | 727 | 2799 | 2799
Total Alkalinity, as CaCO3 | 10 | 39 | 27 | 20 | 45 | 32 | 29 | 30 | 30 | 30-500 (OG) | 742 | 742 | 741 | 741 | 5 | 5
Total Hardness, as CaCO3 ** | 22.1 | 38.8 | 29.6 | 22.2 | 37.4 | 29.1 | 20.4 | 51.9 | 31.1 | 80-100 (OG) | 14 | 14 | 14 | 14 | 251 | 251 | DWSP did 2 total hardness
Calcium Hardness, as CaCO3 ** | 15.5 | 27.2 | 21.2 | 15.2 | 26.7 | 21 | 13.7 | 29.7 | 22.1 |  | 13 | 13 | 13 | 13 | 249 | 249 | but no Ca or Mg hardness
Magnesium Hardness, as CaCO3 ** | 6.6 | 11.5 | 9 | 6.6 | 10.7 | 8.7 | 939 | 11.9 | 8.9 |  | 13 | 13 | 13 | 13 | 249 | 249
Ammonia Nitrogen, N | < 0.01 | 0.11 | 0.01 | < 0.01 | 0.06 | < 0.01 | < 0.01 | 0.12 | 0.01 |  | 733 | 733 | 670 | 670 | 257 | 257
Total Kjeldahl Nitrogen, N | 0.26 | 0.31 | 0.28 | 0.33 | 0.38 | 0.36 | 0.26 | 0.67 | 0.37 |  | 4 | 4 | 4 | 4 | 355 | 355
Organic Nitrogen, N** | 0.22 | 0.27 | 0.26 | 0.33 | 0.39 | 0.35 | 0.23 | 0.56 | 0.35 | 0.15 (OG) | 4 | 4 | 4 | 4 | 229 | 229
Nitrates, N | 0.09 | 0.26 | 0.15 | 0.09 | 0.25 | 0.15 | 0.07 | 0.3 | 0.14 | 10 | 15 | 15 | 15 | 15 | 357 | 357
Nitrites, N | < 0.02 | < 0.02 | < 0.02 | < 0.02 | < 0.02 | < 0.02 | < 0.02 | 0.14 | < 0.02 | 1 | 15 | 15 | 15 | 15 | 357 | 357
Suspended Solids | < 2 | 35 | 7 | --- | --- | --- | --- | --- | --- |  | 12 | 12 | --- | --- | --- | ---
Langelier's Index** | -2.1 | -1.2 | -1.7 | -2.1 | -1.2 | -1.7 | --- | --- | --- |  | 13 | 13 | 13 | 13 | --- | ---
Conductivity Micromhos/cm @ 25 oC | 48 | 120 | 76 | 106 | 173 | 136 | 139 | 144 | 142 |  | 15 | 15 | 15 | 15 | 5 | 5
Chloramine (Total chlorine) | --- | --- | --- | 1.54 | 2.49 | 1.9188 | 0.1 | 2.3 | 1.5421 | 3 | --- | --- | 727 | 727 | 9875 | 9875
C-T Disinfection** (mg/L-min) | --- | --- | --- | 40.233 | 208 | 85.2998 | --- | --- | --- |  | --- | --- | 727 | 727 | --- | ---
Log Giardia Disinfection | --- | --- | --- | 1.04 | 12.19 | 3.8049 | --- | --- | --- | 0.5-log | --- | --- | 727 | 727 | --- | ---
Log Virus Disinfection | --- | --- | --- | 12.13 | >> 20.0 | > 20.0 | --- | --- | --- | 3.0-log | --- | --- | 727 | 727 | --- | ---
Aluminium, Al | 0.068 | 6.13 | 0.59417 | 0.0159 | 0.0965 | 0.049427 | 0.0165 | 0.2876 | 0.093586 | 0.100 (OG) | 15 | 15 | 15 | 15 | 259 | 259
Antimony, Sb | < 0.0002 | 0.0007 | < 0.0002 | < 0.0002 | 0.001 | < 0.0002 | < 0.0002 | 0.001 | < 0.0002 | 0.006 | 15 | 12 | 15 | 15 | 259 | 259
Arsenic, As | < 0.0002 | 0.001 | 0.00067333 | < 0.0002 | 0.0004 | 0.00021333 | < 0.0002 | 0.0008 | 0.00028069 | 0.010 / 0.025 | 15 | 15 | 15 | 15 | 259 | 259
Barium, Ba | 0.0134 | 0.021 | 0.016393 | 0.0124 | 0.0167 | 0.014133 | 0.0106 | 0.0195 | 0.014254 | 1 | 15 | 15 | 15 | 15 | 259 | 259
Beryllium, Be | < 0.0001 | 0.0005 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | 0.0001 | < 0.0001 |  | 15 | 15 | 15 | 15 | 259 | 259
Boron, B | 0.005 | 0.0108 | 0.0076 | 0.0047 | 0.0093 | 0.0070133 | 0.0044 | 0.0279 | 0.0076398 | 5 | 15 | 15 | 15 | 15 | 259 | 259
Bromate, BrO3 **** | < 0.003 | < 0.003 | < 0.003 | < 0.003 | < 0.003 | < 0.003 | < 0.003 | < 0.003 | < 0.003 | 0.01 | 4 | 4 | 4 | 4 | 8 | 8
Bromide, Br **** | 0.019 | 0.03 | 0.02325 | 0.012 | 0.022 | 0.01625 | 0.011 | 0.019 | 0.01575 |  | 4 | 4 | 4 | 4 | 8 | 8
Cadmium, Cd | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | 0.005 | 15 | 15 | 15 | 15 | 259 | 259
Calcium, Ca | 6.2 | 10.9 | 8.4731 | 6.1 | 10.7 | 8.3962 | 5.5 | 11.9 | 8.8687 |  | 13 | 13 | 13 | 13 | 249 | 249
Chlorate, ClO3 **** | < 0.01 | < 0.01 | < 0.01 | 0.04 | 0.14 | 0.095 | 0.05 | 0.22 | 0.12 | 1 | 4 | 4 | 4 | 4 | 8 | 8
Chloride, Cl | 1.8 | 7.7 | 3.58 | 2.3 | 9.3 | 5.5667 | 3.6 | 9.6 | 5.4552 | 250.0 (AO) | 15 | 15 | 15 | 15 | 357 | 357
Chlorite, ClO2 **** | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | 1 | 4 | 4 | 4 | 4 | 8 | 8
Chromium, Cr | 0.0002 | 0.0058 | 0.0010167 | < 0.0001 | 0.0002 | 0.00012083 | < 0.0001 | 0.0022 | 0.00018123 | 0.05 | 15 | 12 | 15 | 12 | 259 | 253
Chlormium VI | 6e-05 | 0.00014 | 8.5e-05 | 6e-05 | 0.0001 | 7.5e-05 | --- | --- | --- |  | 4 | 4 | 4 | 4 | --- | ---
Cobalt, Co | < 0.0001 | 0.0004 | 0.00013 | < 0.0001 | 0.0002 | < 0.0001 | < 0.0001 | 0.0004 | < 0.0001 |  | 15 | 15 | 15 | 15 | 259 | 259
Copper, Cu | 0.0183 | 0.0459 | 0.031987 | 0.0007 | 0.0024 | 0.0013467 | < 0.0005 | 0.0571 | 0.002867 | 1.0000 (AO) | 15 | 15 | 15 | 15 | 259 | 259
Cyanide, CN | < 0.002 | < 0.002 | < 0.002 | < 0.002 | < 0.002 | < 0.002 | < 0.002 | 0.002 | < 0.002 | 0.2 | 4 | 4 | 4 | 4 | 8 | 8
Dissolved Inorganic Carbon | 4.1 | 6.7 | 5.7 | 4.8 | 7.2 | 6.0667 | --- | --- | --- |  | 3 | 3 | 3 | 3 | --- | ---
Dissolved Organic Carbon | 2.65 | 8.34 | 6.8933 | 2.2 | 3.41 | 2.87 | 2.98 | 3.14 | 3.048 | 5.0 (AO) | 15 | 15 | 15 | 15 | 5 | 5
Fluoride, F | 0.04 | 0.08 | 0.056 | 0.03 | 0.79 | 0.66511 | 0.02 | 0.76 | 0.63464 | 1.5 | 15 | 15 | 632 | 632 | 248 | 248
Iron, Fe | 0.0995 | 0.5821 | 0.26944 | < 0.006 | 0.0571 | 0.016333 | < 0.006 | 0.2002 | 0.024253 | 0.300 (AO) | 15 | 15 | 15 | 15 | 258 | 258
Lead, Pb | < 0.0001 | 0.0006 | 0.00021667 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | 0.0032 | 0.00010753 | 0.01 | 15 | 15 | 15 | 15 | 259 | 259
Magnesium, Mg | 1.6 | 2.8 | 2.1754 | 1.6 | 2.6 | 2.1108 | 1.6 | 2.9 | 2.1614 |  | 13 | 13 | 13 | 13 | 249 | 249
Manganese, Mn | 0.0067 | 0.0216 | 0.012573 | 0.0006 | 0.0066 | 0.0023867 | 0.0003 | 0.028 | 0.0031216 | 0.050 (AO) | 15 | 15 | 15 | 15 | 259 | 259
Mercury, Hg | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | 0.001 | 12 | 12 | 12 | 12 | 252 | 252
Molybdenum, Mo | < 0.0005 | 0.001 | < 0.0005 | < 0.0005 | < 0.0005 | < 0.0005 | < 0.0005 | 0.0006 | < 0.0005 |  | 15 | 15 | 15 | 15 | 259 | 259
Nickel, Ni | < 0.0001 | 0.0015 | 0.00082 | < 0.0001 | 0.0009 | 0.00038 | < 0.0001 | 0.0426 | 0.00074324 |  | 15 | 15 | 15 | 15 | 259 | 259
Phosphates, PO4 | 0.0014 | 0.0062 | 0.0032667 | < 0.0005 | 0.0023 | 0.0012167 | < 0.002 | 0.002 | < 0.002 |  | 3 | 3 | 3 | 3 | 78 | 78
Phosphorus (Total), P | --- | --- | --- | --- | --- | --- | < 0.005 | 0.01 | < 0.005 |  | --- | --- | --- | --- | 85 | 85
Potassium, K | 0.62 | 1 | 0.72077 | 0.59 | 0.83 | 0.66077 | 0.48 | 0.91 | 0.66787 |  | 17 | 17 | 17 | 17 | 159 | 159
Selenium, Se | < 0.0002 | 0.0006 | 0.00024 | < 0.0002 | 0.0005 | < 0.0002 | < 0.0002 | 0.0007 | < 0.0002 | 0.01 | 19 | 13 | 19 | 13 | 176 | 165
Silicate, Si02 | 2.12 | 2.6 | 2.36 | 2.22 | 2.64 | 2.44 | --- | --- | --- |  | 3 | 3 | 3 | 3 | --- | ---
Silver, Ag | < 0.0001 | 0.0005 | < 0.0001 | < 0.0001 | 0.0002 | < 0.0001 | < 0.0001 | 0.0004 | < 0.0001 |  | 15 | 15 | 15 | 15 | 259 | 259
Sodium, Na | 2.3 | 5.4 | 3.2477 | 12.1 | 18.8 | 14.9692 | 12.4 | 23.6 | 16.2863 | 20, 200(AO) | 13 | 13 | 13 | 13 | 249 | 249
Strontium, Sr | 0.032 | 0.062 | 0.042067 | 0.0322 | 0.0591 | 0.04186 | 0.0297 | 0.1211 | 0.042447 |  | 15 | 15 | 15 | 15 | 259 | 259
Sulphate, SO4 | 4.5 | 31.1 | 7.1733 | 19.1 | 31.5 | 25.5667 | 18.4 | 38.9 | 26.6328 | 500.0 (AO) | 15 | 15 | 15 | 15 | 357 | 357
Thallium, Tl | < 0.0001 | 0.0003 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 |  | 15 | 15 | 15 | 15 | 259 | 259
Tin, Sn | < 0.0002 | 0.0003 | < 0.0002 | < 0.0002 | 0.0004 | < 0.0002 | < 0.0002 | 0.0084 | < 0.0002 |  | 12 | 12 | 12 | 12 | 253 | 253
Titanium, Ti | 0.0018 | 0.0287 | 0.0088133 | < 0.0002 | < 0.0002 | < 0.0002 | < 0.0002 | 0.0046 | < 0.0002 |  | 15 | 15 | 15 | 15 | 259 | 259
Tungsten, W | < 0.0002 | 0.0007 | 0.00021667 | < 0.0002 | 0.0003 | 0.00025 | < 0.0002 | 0.0006 | < 0.0002 |  | 12 | 12 | 12 | 12 | 253 | 253
Uranium, U | < 0.0001 | 0.0005 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | 0.0002 | < 0.0001 | 0.02 | 15 | 15 | 15 | 15 | 259 | 259
Vanadium, V | 0.0004 | 0.0042 | 0.00081333 | < 0.0001 | 0.0005 | 0.00023 | < 0.0001 | 0.0005 | 0.00033378 |  | 15 | 15 | 15 | 15 | 259 | 259
Zinc, Zn | < 0.0005 | < 0.0005 | < 0.0005 | < 0.0005 | 0.0018 | 0.00072 | < 0.0005 | 0.0543 | 0.001466 | 5.000 (AO) | 15 | 15 | 15 | 15 | 259 | 259
Zirconium, Zr | 0.0001 | 0.001 | 0.00031667 | < 0.0001 | 0.0002 | 0.00016667 | < 0.0001 | 0.0003 | < 0.0001 |  | 12 | 12 | 12 | 12 | 253 | 253
Total Trihalomethanes *** | --- | --- | --- | 0.0182 | 0.0366 | 0.03118 | 0.0202 | 0.0542 | 0.0393 | 0.1 | 3 | 3 | 15 | 15 | 39 | 39
Haloacetic Acids (5) | --- | --- | --- | 0.0154 | 0.0295 | 0.0219 | 0.018 | 0.0455 | 0.0275 | 0.08 | --- | --- | 15 | 15 | 39 | 39
Haloacetic Acids (9) | --- | --- | --- | 0.0194 | 0.0338 | 0.0261 | 0.021 | 0.0512 | 0.0313 |  | --- | --- | 15 | 15 | 39 | 39
MICROBIOLOGICAL | MIN. | MAX. | AVERAGE | MIN. | MAX. | # >MAC | MIN. | MAX. | # >MAC
Total Coliforms (CFU/100 mL) | 0 | < 2420 | 677 | 0 | 0 | 0 | 0 | Positive | 15 | 0 | 363 | 363 | 1439 | 1439 | 4989 | 4989
E. Coli (CFU/100 mL) | 0 | 207 | 32 | 0 | 0 | 0 | 0 | Positive | 1 | 0 | 363 | 363 | 1439 | 1439 | 4989 | 4989
HPC (CFU/mL) | < 10 | > 3000 | 344 | < 10 | 60 | 0 | < 10 | 2000 | 13 | 500 (OG) | 53 | 53 | 208 | 208 | 2883 | 2883
| MIN. | MAX. | AVERAGE | MIN. | MAX. | AVERAGE | MIN. | MAX. | AVERAGE
Cryptosporidium (No. per 100 L) | 0 | 5.7 | 1.2 | 0 | 0 | 0 | --- | --- | --- |  | 12 | 12 | 12 | 12 | --- | ---
Giardia (No. per 100L) | 0 | 17.1 | 4.7667 | 0 | 0 | 0 | --- | --- | --- |  | 12 | 12 | 12 | 12 | --- | ---
RADIOLOGICAL
Gross-Alpha Radioactivity (Bq/L) **** | < 0.04 | < 0.04 | < 0.04 | < 0.01 | 0.03 | < 0.01 | --- | --- | --- | 0.5 | 3 | 3 | 55 | 52 | --- | ---
Gross-Beta Radioactivity (Bq/L) | < 0.04 | < 0.04 | < 0.04 | < 0.01 | 0.053 | 0.037231 | --- | --- | --- | 1 | 3 | 3 | 55 | 52 | --- | ---
Tritium (Bq/L) | < 5.0 | < 5.0 | < 5.0 | < 3.0 | 6 | 4.3025 | --- | --- | --- | 7000 | 3 | 3 | 55 | 52 | --- | ---
Total # of Results | [10 empty] | 5880 |  | 11082 |  |  | 42609
* Guidelines for Canadian Drinking Water Quality (Health Canada) & Ontario Drinking Water Standards (Ministry of the Environment)
**calculated parameter
*** The reported Average Total THM value is an annual average of the maximum value observed in each quarter
**** Detection limits are different not the same for all sample locations for this parameter
M.A.C. - Maximum Allowable Concentration from drinking water guidelines
MAC for Arsenic from the Guidelines for Canadian Drinking Water Quality is 0.010 mg/L, from the Ontario Drinking Water Standards is 0.025 mg/L | [9 empty] | mg/L = milligrams per Litre = parts per million (ppm)
< Indicates value below analytical detection limit | [9 empty] | TCU = true colour units
NL - No limit exists under provincial or federal drinking water guidelines | [9 empty] | NTU = nephelometric turbidity units
--- No data available (test not performed) | [9 empty] | Bq/L = Becquerels per Litre
AO = Aesthetic Objective
Average 2013 Water Production Rate: BRITANNIA = 145.0 ML/d; LEMIEUX = 130.3 ML/d; TOTAL = 275.3 ML/d | [9 empty] | OG = Operational Guideline

## Both 2013
2013 City of Ottawa Drinking Water Quality : Physical, Chemical, Microbiological & Radiological
Britannia and Lemieux Island Water Purification Plants & Distribution System
PARAMETER | BRITANNIA |  |  | LEMIEUX ISLAND |  |  | BRITANNIA |  |  | LEMIEUX ISLAND |  |  | CENTRAL |  |  | M.A.C.* | TOTAL # of RESULTS
(mg/L unless otherwise stated) | RAW (RIVER) WATER |  |  | RAW (RIVER) WATER |  |  | TREATED WATER |  |  | TREATED WATER |  |  | DISTRIBUTION |  |  | TREATED | Brit Raw Water |  | Brit Treated Water |  | Lem Raw Water |  | Lem Treated Water |  | Central Dist
| MIN. | MAX. | AVERAGE | MIN. | MAX. | AVERAGE | MIN. | MAX. | AVERAGE | MIN. | MAX. | AVERAGE | MIN. | MAX. | AVERAGE | WATER | # Tested | # Used | # Tested | # Used | # Tested | # Used | # Tested | # Used | # Tested | # Used
PHYSICAL
Colour, T.C.U. | 32 | 61 | 42 | 32 | 55 | 42 | < 3 | 6.8 | < 3 | < 3 | 4 | < 3 | < 3 | 5 | < 3 | 5.0 (AO) | 13 | 13 | 732 | 732 | 13 | 13 | 716 | 716 | 7 | 7
Turbidity, N.T.U. | 1.22 | 10.47 | 3.38 | 1.32 | 12 | 3.63 | 0.02 | 0.09 | 0.06 | 0.02 | 0.11 | 0.05 | 0.06 | 7.02 | 0.21 | 5.00 (AO) | 729 | 729 | 728 | 728 | 728 | 728 | 727 | 727 | 2883 | 2883
Temperature, oC | < 0.1 | 26.1 | 9.9 | < 0.01 | 26.5 | 9.6 | --- | --- | --- | --- | --- | --- | 0.2 | 26.4 | 12.7 | 15.0 (AO) | 728 | 728 | --- | --- | 728 | 728 | --- | --- | 2803 | 2803
UV 254 (cm-1) | 0.228 | 0.382 | 0.284 | 0.238 | 0.348 | 0.281 | 0.06 | 0.06 | 0.06 | 0.04 | 0.05 | 0.04 | 0.04 | 0.07 | 0.051 |  | 728 | 728 | 4 | 4 | 726 | 726 | 4 | 4 | 7 | 7
CHEMICAL INORGANIC
pH | 6.9 | 7.66 | 7.35 | 6.88 | 7.9 | 7.44 | 9.11 | 9.57 | 9.36 | 9.05 | 10.06 | 9.36 | 8.75 | 9.89 | 9.32 | 6.5-8.5 (OG) | 732 | 732 | 729 | 729 | 731 | 731 | 727 | 727 | 2799 | 2799
Total Alkalinity, as CaCO3 | 15 | 44 | 28 | 10 | 39 | 27 | 22 | 52 | 34 | 20 | 45 | 32 | 29 | 30 | 30 | 30-500 (OG) | 745 | 745 | 744 | 744 | 742 | 742 | 741 | 741 | 5 | 5
Total Hardness, as CaCO3 ** | 22.7 | 40.9 | 31.8 | 22.1 | 38.8 | 29.6 | 22.7 | 40 | 31.8 | 22.2 | 37.4 | 29.1 | 20.4 | 51.9 | 31.1 | 80-100 (OG) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 251 | 251 | DWSP did 2 total hardness
Calcium Hardness, as CaCO3 ** | 15.7 | 29 | 22.1 | 15.5 | 27.2 | 21.2 | 15.7 | 28.5 | 22.2 | 15.2 | 26.7 | 21 | 13.7 | 29.7 | 22.1 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 249 | 249 | but no Ca or Mg hardness
Magnesium Hardness, as CaCO3 ** | 7 | 11.9 | 9.3 | 6.6 | 11.5 | 9 | 7 | 11.5 | 9.2 | 6.6 | 10.7 | 8.7 | 939 | 11.9 | 8.9 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 249 | 249
Ammonia Nitrogen, N | < 0.01 | 0.09 | 0.02 | < 0.01 | 0.11 | 0.01 | < 0.01 | 0.08 | < 0.01 | < 0.01 | 0.06 | < 0.01 | < 0.01 | 0.12 | 0.01 |  | 733 | 733 | 744 | 744 | 733 | 733 | 670 | 670 | 257 | 257
Total Kjeldahl Nitrogen, N | 0.25 | 0.57 | 0.31 | 0.26 | 0.31 | 0.28 | 0.3 | 0.48 | 0.36 | 0.33 | 0.38 | 0.36 | 0.26 | 0.67 | 0.37 |  | 12 | 12 | 12 | 12 | 4 | 4 | 4 | 4 | 355 | 355
Organic Nitrogen, N** | 0.24 | 0.56 | 0.29 | 0.22 | 0.27 | 0.26 | 0.3 | 0.48 | 0.35 | 0.33 | 0.39 | 0.35 | 0.23 | 0.56 | 0.35 | 0.15 (OG) | 12 | 12 | 12 | 12 | 4 | 4 | 4 | 4 | 229 | 229
Nitrates, N | 0.07 | 0.25 | 0.15 | 0.09 | 0.26 | 0.15 | 0.09 | 0.26 | 0.16 | 0.09 | 0.25 | 0.15 | 0.07 | 0.3 | 0.14 | 10 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 357 | 357
Nitrites, N | < 0.02 | < 0.02 | < 0.02 | < 0.02 | < 0.02 | < 0.02 | < 0.02 | < 0.02 | < 0.02 | < 0.02 | < 0.02 | < 0.02 | < 0.02 | 0.14 | < 0.02 | 1 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 357 | 357
Suspended Solids | < 2 | 65 | 8 | < 2 | 35 | 7 | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 11 | 11 | --- | --- | 12 | 12 | --- | --- | --- | ---
Langelier's Index** | -2.2 | -1.4 | -1.7 | -2.1 | -1.2 | -1.7 | -2.2 | -1.4 | -1.7 | -2.1 | -1.2 | -1.7 | --- | --- | --- |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | --- | ---
Conductivity Micromhos/cm @ 25 oC | 58 | 104 | 77 | 48 | 120 | 76 | 108 | 183 | 146 | 106 | 173 | 136 | 139 | 144 | 142 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 5 | 5
Chloramine (Total chlorine) | --- | --- | --- | --- | --- | --- | 1.54 | 2.53 | 1.9022 | 1.54 | 2.49 | 1.9188 | 0.1 | 2.3 | 1.5421 | 3 | --- | --- | 729 | 729 | --- | --- | 727 | 727 | 9875 | 9875
C-T Disinfection** (mg/L-min) | --- | --- | --- | --- | --- | --- | 32.1 | 130.1 | 62.0035 | 40.233 | 208 | 85.2998 | --- | --- | --- |  | --- | --- | 1453 | 1453 | --- | --- | 727 | 727 | --- | ---
Log Giardia Disinfection | --- | --- | --- | --- | --- | --- | 0.8 | 9.79 | 2.9745 | 1.04 | 12.19 | 3.8049 | --- | --- | --- | 0.5-log | --- | --- | 1453 | 1453 | --- | --- | 727 | 727 | --- | ---
Log Virus Disinfection | --- | --- | --- | --- | --- | --- | 3.66 | >> 20.0 | > 20.0 | 12.13 | >> 20.0 | > 20.0 | --- | --- | --- | 3.0-log | --- | --- | 1453 | 1453 | --- | --- | 727 | 727 | --- | ---
Aluminium, Al | 0.104 | 0.6653 | 0.22527 | 0.068 | 6.13 | 0.59417 | 0.0317 | 0.2755 | 0.11952 | 0.0159 | 0.0965 | 0.049427 | 0.0165 | 0.2876 | 0.093586 | 0.100 (OG) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 259 | 259
Antimony, Sb | < 0.0002 | < 0.0002 | < 0.0002 | < 0.0002 | 0.0007 | < 0.0002 | < 0.0002 | 0.0011 | < 0.0002 | < 0.0002 | 0.001 | < 0.0002 | < 0.0002 | 0.001 | < 0.0002 | 0.006 | 15 | 12 | 15 | 15 | 15 | 12 | 15 | 15 | 259 | 259
Arsenic, As | < 0.0002 | 0.001 | 0.00064 | < 0.0002 | 0.001 | 0.00067333 | < 0.0002 | 0.0007 | 0.00028667 | < 0.0002 | 0.0004 | 0.00021333 | < 0.0002 | 0.0008 | 0.00028069 | 0.010 / 0.025 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 259 | 259
Barium, Ba | 0.0137 | 0.0313 | 0.017227 | 0.0134 | 0.021 | 0.016393 | 0.0119 | 0.0171 | 0.014213 | 0.0124 | 0.0167 | 0.014133 | 0.0106 | 0.0195 | 0.014254 | 1 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 259 | 259
Beryllium, Be | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | 0.0005 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | 0.0001 | < 0.0001 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 259 | 259
Boron, B | 0.0048 | 0.0113 | 0.0075333 | 0.005 | 0.0108 | 0.0076 | 0.0046 | 0.0082 | 0.0069333 | 0.0047 | 0.0093 | 0.0070133 | 0.0044 | 0.0279 | 0.0076398 | 5 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 259 | 259
Bromate, BrO3 **** | < 0.003 | < 0.003 | < 0.003 | < 0.003 | < 0.003 | < 0.003 | < 0.003 | < 0.003 | < 0.003 | < 0.003 | < 0.003 | < 0.003 | < 0.003 | < 0.003 | < 0.003 | 0.01 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 8 | 8
Bromide, Br **** | 0.02 | 0.024 | 0.02225 | 0.019 | 0.03 | 0.02325 | 0.014 | 0.022 | 0.01725 | 0.012 | 0.022 | 0.01625 | 0.011 | 0.019 | 0.01575 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 8 | 8
Cadmium, Cd | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | 0.005 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 259 | 259
Calcium, Ca | 6.3 | 11.6 | 8.8615 | 6.2 | 10.9 | 8.4731 | 6.3 | 11.4 | 8.9 | 6.1 | 10.7 | 8.3962 | 5.5 | 11.9 | 8.8687 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 249 | 249
Chlorate, ClO3 **** | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | 0.07 | 0.16 | 0.105 | 0.04 | 0.14 | 0.095 | 0.05 | 0.22 | 0.12 | 1 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 8 | 8
Chloride, Cl | 2.4 | 8.3 | 3.64 | 1.8 | 7.7 | 3.58 | 4 | 10.2 | 5.6733 | 2.3 | 9.3 | 5.5667 | 3.6 | 9.6 | 5.4552 | 250.0 (AO) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 357 | 357
Chlorite, ClO2 **** | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | < 0.01 | 1 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 8 | 8
Chromium, Cr | 0.0003 | 0.0015 | 0.00065 | 0.0002 | 0.0058 | 0.0010167 | < 0.0001 | 0.0004 | 0.00017083 | < 0.0001 | 0.0002 | 0.00012083 | < 0.0001 | 0.0022 | 0.00018123 | 0.05 | 15 | 12 | 15 | 12 | 15 | 12 | 15 | 12 | 259 | 253
Chlormium VI | 6e-05 | 9e-05 | 7.25e-05 | 6e-05 | 0.00014 | 8.5e-05 | 4e-05 | 8e-05 | 5.75e-05 | 6e-05 | 0.0001 | 7.5e-05 | --- | --- | --- |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | --- | ---
Cobalt, Co | < 0.0001 | 0.0006 | 0.00012 | < 0.0001 | 0.0004 | 0.00013 | < 0.0001 | 0.0002 | < 0.0001 | < 0.0001 | 0.0002 | < 0.0001 | < 0.0001 | 0.0004 | < 0.0001 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 259 | 259
Copper, Cu | 0.0075 | 0.0373 | 0.020673 | 0.0183 | 0.0459 | 0.031987 | < 0.0005 | 0.0019 | 0.00094333 | 0.0007 | 0.0024 | 0.0013467 | < 0.0005 | 0.0571 | 0.002867 | 1.0000 (AO) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 259 | 259
Cyanide, CN | < 0.002 | < 0.002 | < 0.002 | < 0.002 | < 0.002 | < 0.002 | < 0.002 | < 0.002 | < 0.002 | < 0.002 | < 0.002 | < 0.002 | < 0.002 | 0.002 | < 0.002 | 0.2 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 8 | 8
Dissolved Inorganic Carbon | 3.5 | 6.9 | 5.6333 | 4.1 | 6.7 | 5.7 | 4.5 | 7.2 | 6.2667 | 4.8 | 7.2 | 6.0667 | --- | --- | --- |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | --- | ---
Dissolved Organic Carbon | 6.68 | 8.09 | 7.176 | 2.65 | 8.34 | 6.8933 | 2.8 | 3.74 | 3.1353 | 2.2 | 3.41 | 2.87 | 2.98 | 3.14 | 3.048 | 5.0 (AO) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 5 | 5
Fluoride, F | 0.04 | 0.08 | 0.056667 | 0.04 | 0.08 | 0.056 | 0.58 | 0.792 | 0.68779 | 0.03 | 0.79 | 0.66511 | 0.02 | 0.76 | 0.63464 | 1.5 | 15 | 15 | 735 | 735 | 15 | 15 | 632 | 632 | 248 | 248
Iron, Fe | 0.1375 | 1.094 | 0.29335 | 0.0995 | 0.5821 | 0.26944 | < 0.006 | 0.014 | 0.00774 | < 0.006 | 0.0571 | 0.016333 | < 0.006 | 0.2002 | 0.024253 | 0.300 (AO) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 258 | 258
Lead, Pb | < 0.0001 | 0.002 | 0.00033 | < 0.0001 | 0.0006 | 0.00021667 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | 0.0032 | 0.00010753 | 0.01 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 259 | 259
Magnesium, Mg | 1.7 | 2.9 | 2.2569 | 1.6 | 2.8 | 2.1754 | 1.7 | 2.8 | 2.2369 | 1.6 | 2.6 | 2.1108 | 1.6 | 2.9 | 2.1614 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 249 | 249
Manganese, Mn | 0.0079 | 0.3368 | 0.033453 | 0.0067 | 0.0216 | 0.012573 | 0.0011 | 0.0059 | 0.0030533 | 0.0006 | 0.0066 | 0.0023867 | 0.0003 | 0.028 | 0.0031216 | 0.050 (AO) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 259 | 259
Mercury, Hg | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | < 0.00005 | 0.001 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 252 | 252
Molybdenum, Mo | < 0.0005 | < 0.0005 | < 0.0005 | < 0.0005 | 0.001 | < 0.0005 | < 0.0005 | < 0.0005 | < 0.0005 | < 0.0005 | < 0.0005 | < 0.0005 | < 0.0005 | 0.0006 | < 0.0005 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 259 | 259
Nickel, Ni | < 0.0001 | 0.0065 | 0.00123 | < 0.0001 | 0.0015 | 0.00082 | < 0.0001 | 0.0013 | 0.00048 | < 0.0001 | 0.0009 | 0.00038 | < 0.0001 | 0.0426 | 0.00074324 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 259 | 259
Phosphates, PO4 | 0.0017 | 0.0058 | 0.0041333 | 0.0014 | 0.0062 | 0.0032667 | 0.0016 | 0.0043 | 0.0033333 | < 0.0005 | 0.0023 | 0.0012167 | < 0.002 | 0.002 | < 0.002 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 78 | 78
Phosphorus (Total), P | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | < 0.005 | 0.01 | < 0.005 |  | --- | --- | --- | --- | --- | --- | --- | --- | 85 | 85
Potassium, K | 0.63 | 0.86 | 0.71462 | 0.62 | 1 | 0.72077 | 0.61 | 0.76 | 0.66462 | 0.59 | 0.83 | 0.66077 | 0.48 | 0.91 | 0.66787 |  | 16 | 16 | 16 | 16 | 17 | 17 | 17 | 17 | 159 | 159
Selenium, Se | < 0.0002 | 0.0006 | < 0.0002 | < 0.0002 | 0.0006 | 0.00024 | < 0.0002 | 0.0006 | 0.00022 | < 0.0002 | 0.0005 | < 0.0002 | < 0.0002 | 0.0007 | < 0.0002 | 0.01 | 21 | 15 | 21 | 15 | 19 | 13 | 19 | 13 | 176 | 165
Silicate, Si02 | 2.2 | 2.52 | 2.3733 | 2.12 | 2.6 | 2.36 | 2.36 | 2.64 | 2.5067 | 2.22 | 2.64 | 2.44 | --- | --- | --- |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | --- | ---
Silver, Ag | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | 0.0005 | < 0.0001 | < 0.0001 | 0.0002 | < 0.0001 | < 0.0001 | 0.0002 | < 0.0001 | < 0.0001 | 0.0004 | < 0.0001 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 259 | 259
Sodium, Na | 2.6 | 6 | 3.3538 | 2.3 | 5.4 | 3.2477 | 13 | 22.5 | 17 | 12.1 | 18.8 | 14.9692 | 12.4 | 23.6 | 16.2863 | 20, 200(AO) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 249 | 249
Strontium, Sr | 0.0319 | 0.063 | 0.04136 | 0.032 | 0.062 | 0.042067 | 0.0318 | 0.0623 | 0.041167 | 0.0322 | 0.0591 | 0.04186 | 0.0297 | 0.1211 | 0.042447 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 259 | 259
Sulphate, SO4 | 4.7 | 7.2 | 5.6467 | 4.5 | 31.1 | 7.1733 | 19.4 | 35.2 | 27.82 | 19.1 | 31.5 | 25.5667 | 18.4 | 38.9 | 26.6328 | 500.0 (AO) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 357 | 357
Thallium, Tl | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | 0.0003 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 259 | 259
Tin, Sn | < 0.0002 | 0.0003 | < 0.0002 | < 0.0002 | 0.0003 | < 0.0002 | < 0.0002 | 0.0011 | < 0.0002 | < 0.0002 | 0.0004 | < 0.0002 | < 0.0002 | 0.0084 | < 0.0002 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 253 | 253
Titanium, Ti | 0.0033 | 0.0402 | 0.0095067 | 0.0018 | 0.0287 | 0.0088133 | < 0.0002 | < 0.0002 | < 0.0002 | < 0.0002 | < 0.0002 | < 0.0002 | < 0.0002 | 0.0046 | < 0.0002 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 259 | 259
Tungsten, W | < 0.0002 | 0.0005 | < 0.0002 | < 0.0002 | 0.0007 | 0.00021667 | < 0.0002 | 0.0003 | < 0.0002 | < 0.0002 | 0.0003 | 0.00025 | < 0.0002 | 0.0006 | < 0.0002 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 253 | 253
Uranium, U | < 0.0001 | 0.0002 | < 0.0001 | < 0.0001 | 0.0005 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | < 0.0001 | 0.0002 | < 0.0001 | 0.02 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 259 | 259
Vanadium, V | 0.0005 | 0.002 | 0.00067333 | 0.0004 | 0.0042 | 0.00081333 | < 0.0001 | 0.0006 | 0.00034 | < 0.0001 | 0.0005 | 0.00023 | < 0.0001 | 0.0005 | 0.00033378 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 259 | 259
Zinc, Zn | < 0.0005 | < 0.0005 | < 0.0005 | < 0.0005 | < 0.0005 | < 0.0005 | < 0.0005 | 0.0032 | 0.00094 | < 0.0005 | 0.0018 | 0.00072 | < 0.0005 | 0.0543 | 0.001466 | 5.000 (AO) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 259 | 259
Zirconium, Zr | 0.0001 | 0.0003 | 0.0002 | 0.0001 | 0.001 | 0.00031667 | < 0.0001 | 0.0003 | < 0.0001 | < 0.0001 | 0.0002 | 0.00016667 | < 0.0001 | 0.0003 | < 0.0001 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 253 | 253
Total Trihalomethanes *** | --- | --- | --- | --- | --- | --- | 0.0208 | 0.0443 | 0.03428 | 0.0182 | 0.0366 | 0.03118 | 0.0202 | 0.0542 | 0.0393 | 0.1 | 3 | 3 | 15 | 15 | 3 | 3 | 15 | 15 | 39 | 39
Haloacetic Acids (5) | --- | --- | --- | --- | --- | --- | 0.0175 | 0.0317 | 0.0248 | 0.0154 | 0.0295 | 0.0219 | 0.018 | 0.0455 | 0.0275 | 0.08 | --- | --- | 15 | 15 | --- | --- | 15 | 15 | 39 | 39
Haloacetic Acids (9) | --- | --- | --- | --- | --- | --- | 0.0218 | 0.0365 | 0.0291 | 0.0194 | 0.0338 | 0.0261 | 0.021 | 0.0512 | 0.0313 |  | --- | --- | 15 | 15 | --- | --- | 15 | 15 | 39 | 39
MICROBIOLOGICAL | MIN. | MAX. | AVERAGE | MIN. | MAX. | AVERAGE | MIN. | MAX. | # >MAC | MIN. | MAX. | # >MAC | MIN. | MAX. | # >MAC
Total Coliforms (CFU/100 mL) | 8 | > 2420 | 821 | 0 | < 2420 | 677 | 0 | Positive | 1 | 0 | 0 | 0 | 0 | Positive | 15 | 0 | 365 | 365 | 1427 | 1427 | 363 | 363 | 1439 | 1439 | 4989 | 4989
E. Coli (CFU/100 mL) | 0 | 614 | 25 | 0 | 207 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Positive | 1 | 0 | 365 | 365 | 1427 | 1427 | 363 | 363 | 1439 | 1439 | 4989 | 4989
HPC (CFU/mL) | < 10 | > 3000 | 337 | < 10 | > 3000 | 344 | < 10 | 120 | 0 | < 10 | 60 | 0 | < 10 | 2000 | 13 | 500 (OG) | 53 | 53 | 212 | 212 | 53 | 53 | 208 | 208 | 2883 | 2883
| MIN. | MAX. | AVERAGE | MIN. | MAX. | AVERAGE | MIN. | MAX. | AVERAGE | MIN. | MAX. | AVERAGE | MIN. | MAX. | AVERAGE
Campylobacter (MPN/L) | 0 | 8.86 | 2.1329 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 12 | 12 | --- | --- | --- | --- | --- | --- | --- | ---
E. coli O157:H7 (MPN/L) | 0 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 12 | 12 | --- | --- | --- | --- | --- | --- | --- | ---
Enteric Virus (MPN/L) | 0 | 1.4 | 0.39833 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | 9 | 9 | --- | --- | --- | --- | --- | --- | --- | ---
Cryptosporidium (No. per 100 L) | 0 | 14 | 1.925 | 0 | 5.7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | --- | --- | --- |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | --- | ---
Giardia (No. per 100L) | 0 | 17 | 5.8167 | 0 | 17.1 | 4.7667 | 0 | 0 | 0 | 0 | 0 | 0 | --- | --- | --- |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | --- | ---
RADIOLOGICAL
Gross-Alpha Radioactivity (Bq/L) **** | < 0.04 | < 0.04 | < 0.04 | < 0.04 | < 0.04 | < 0.04 | < 0.01 | 0.02 | < 0.01 | < 0.01 | 0.03 | < 0.01 | --- | --- | --- | 0.5 | 3 | 3 | 55 | 52 | 3 | 3 | 55 | 52 | --- | ---
Gross-Beta Radioactivity (Bq/L) | < 0.04 | < 0.04 | < 0.04 | < 0.04 | < 0.04 | < 0.04 | < 0.01 | 0.049 | 0.032788 | < 0.01 | 0.053 | 0.037231 | --- | --- | --- | 1 | 3 | 3 | 55 | 52 | 3 | 3 | 55 | 52 | --- | ---
Tritium (Bq/L) | < 5.0 | < 5.0 | < 5.0 | < 5.0 | < 5.0 | < 5.0 | < 3.0 | 7 | 4.4301 | < 3.0 | 6 | 4.3025 | --- | --- | --- | 7000 | 3 | 3 | 55 | 52 | 3 | 3 | 55 | 52 | --- | ---
Total # of Results | [16 empty] | 5940 |  | 13458 |  | 5880 |  | 11082 |  |  | 42609
* Guidelines for Canadian Drinking Water Quality (Health Canada) & Ontario Drinking Water Standards (Ministry of the Environment) | [15 empty] | Total # of BritanniaTests: |  |  |  |  | 11820
**calculated parameter | [15 empty] | Total # of LemieuxTests: |  |  |  |  | 24540
*** The reported Average Total THM value is an annual average of the maximum value observed in each quarter | [15 empty] | Total # of Distribution Tests: |  |  |  |  | 42609
**** Detection limits are different not the same for all sample locations for this parameter
MAC - Maximum Acceptable Concentration
MAC for Arsenic from the Guidelines for Canadian Drinking Water Quality is 0.010 mg/L, from the Ontario Drinking Water Standards is 0.025 mg/L | [15 empty] | mg/L = milligrams per Litre = parts per million (ppm)
< Indicates value below analytical detection limit | [15 empty] | TCU = true colour units
NL - No limit exists under provincial or federal drinking water guidelines | [15 empty] | NTU = nephelometric turbidity units
--- No data available (test not performed) | [15 empty] | Bq/L = Becquerels per Litre
AO = Aesthetic Objective
Average 2013 Water Production Rate: BRITANNIA = 145.0 ML/d; LEMIEUX = 130.3 ML/d; TOTAL = 275.3 ML/d | [15 empty] | OG = Operational Guideline